## Calculations SS
Temperature data | Fill in values in grey cells
Minimum temperature at site | -20 | ºC
Maximum temperature at site | 40 | ºC
Temperature when installing cable ladders | 20 | ºC
Calculations | Calculate
Temperature differential | 60 | ºC
Expansion of stainless steel for this temperature range | 0.96 | mm/m
Expansion coupler gap when installing (Including safety factor) | 23.3333 | mm
Maximum spacing between expansion couplers | 41.6667 | m
Constants
Expansion of AISI316L per increased ºC: | 0.016 | mm/mºC
Oglaend expansion coupler allows movement of * | 40 | mm
*60mm - safety factor of 2 x 10 mm = 40 mm working range
| 23.3333 | mm
Only for Stainless Steel installations. |  |  | ØI-RD-UG-EN-0081
Calculation : Installing SS Expansion Couplers
Example of installation in warm weather
Example of installation in cold weather
The gap between the couples when installing is
Note on B3: Fill in temperature
Note on B4: Fill in temperature
Note on B5: Fill in temperature